## Slide 1: Power Plant Technology Combined Cycle and Renewable Energy Power Systems (Lecture 1)
by
Mohamad Firdaus Basrawi, Dr. (Eng) Mechanical Engineering Faculty mfirdausb@ump.edu.my

## Slide 2
Combined cycle
Gas turbine has high temperature and mass flow rate at the exhaust stage.
Steam turbine has lower turbine inlet temperature.
A widely used combination is a gas turbine fuelled by natural gas or synthesis gas from coal, and a steam power plant.
This is called a Combined Cycle Gas Turbine (CCGT) plant.
CCGT can achieve a thermal efficiency of 60%. (a steam power plant is limited to around 35-42%).
Many new gas power plants are of this type.
T3: 900-1400oC
T4: 450-650oC
T3,max: 655oC

## Slide 3
Advantages of combined cycle power plant
High overall plant efficiency
>50%
Low environmental impact
Very low NOx emissions, reduce 60% of CO2 emissions
Low investment cost
30% less than steam power plant per kW basis
Great operating flexibility
Based on Gas Cycle and Simple Steam Cycle makes it possible to start-up and shut-down the plants quickly.
Phased installation
Gas turbine can operate while steam turbine is under construction. This makes it possible to adjust the growth in demand for energy in a grid.

## Slide 4
Brayton-Rankine Combined Cycle
(Combined Cycle Gas Turbine)
The topping plant operating on Bryton and the bottoming one operating on Rankine cycle.

## Slide 5
http://www.tenaskawestmorelandproject.com/howitworks.html
Not found

## Slide 6
Integrated Gasification Combined Cycle (IGCC)
Coal is abundantly available in many countries.
However, coal based steam power plants emit large amount of pollutant.
Gasification technology is available to convert coal to synthetic gas (Syngas)
Since energy depletion and environmental problem became severe, many parties start to use syngas as a fuel for high efficiency CCGT.
It can increase thermal efficiency (energy), emit less emissions (environment), and save fuels and cheap coal can be used (economic).
This type of plant called IGCC. The plant called integrated because:
On-site produced syngas is used as a fuel for CCGT.
Steam produced by the syngas cooler is also used for steam turbine.

## Slide 7
Gasification
Purification
Gas Turbine
Steam Turbine
Steam
Edit arrow
https://commons.wikimedia.org/wiki/File:IGCC_diagram.svg

## Slide 8
http://www.ieefa.org/dukes-edwardsport-igcc-still-dealing-with-technical-problems/
http://www.duke-energy.com/about-us/how-igcc-works.asp
Integrated Gasification Combined Cycle (IGCC)
Power generation (Syngas+N2)
This can reduce flame temperature and therefore thermal NOx can be reduced
Gasification
Coal > CO+CO2+H2
Gas Purification Sulfer + Mercury is removed
Exhaust heat recovery
From Gasification and Gas Turbine
Power Generation
Not found

## Slide 9
Not found

## Slide 10
Efficiency of Combined Cycle power plant

## Slide 11
CC efficiency when heat loss at HRGS is considered
In actual cycle, there is always some heat loss and the heat absorbed is always less than the heat rejected.
The overall plant efficiency is
Therefore,
Heat loss in between two plants in series
xL is fraction of the heat supplied which is lost (QL/Q1)
Heat loss

## Slide 12
The ratio of Q3/Q2 is the efficiency of the boiler in the bottoming plant, so that
Now,
Where x Is the overall efficiency of the bottoming plant

## Slide 13
Series-parallel plants with two cyclic plants in series having supplementary firing
Brayton/Rankine cyclic plants with supplementary heating

## Slide 14
Let the fraction of the total heat supplied that is used for supplementary heating be
(6)

## Slide 15
Series-parallel plans with two cyclic plants in series having supplementary firing and heat loss between the two plants
Brayton/Rankine cyclic plants with supplementary heating
QL

## Slide 16
Let X2 and xL be the fractions of heat supply (Q1) which represent supplementary heat supply (Q4) and heat loss to the surroundings (QL), respectively

## Slide 17
which is the same as Eq. (3.8) derived earlier. It can also be expressed in a different way by defining the boiler efficiency
Therefore, from Eq. (3.13) the overall plant efficiency of the combined plant becomes

## Slide 18
Example
A combined cycle gas turbine uses a simple gas turbine for topping cycle and simple rankine cycle for bottoming cycle. Atmospheric air enters the gas turbine at 101kPa and 20oC, and the maximum gas cycle temperature is 1100oC. The compressor ratio is 8 with isentropic efficiency of 85%. The turbine isentropic efficiency is 90%. The gas stream leaves the heat exchanger at the saturation temperature of the steam flowing through the heat exchanger. Steam flows through the heat exchanger with a pressure of 6MPa, and leaves at 320oC. The steam cycle condenser operates at 20kPa, and the isentropic efficiency of the steam turbine is 90%. Determine the mass flow rate of air through the air compressor required for this system to produce 100MW of power. Use specific heat as 1.005kJ/kgK and specific heat ratio as 1.4.

## Slide 19
T7=1100oC
P1=P4=0.02MPa
P2=P3=6.0MPa
T3=320oC
ƞs,T =90%
ƞs,C =85%
rC =8
P5=0.101MPa
T5=20oC
No heat losses at HE
From Net work relation
cp=1.005kJ/kg
k=1.4
Wnet=100MW
From heat balance relation at heat exchanger
GC: T8, T9, T7, T6, T5
SC: h3, h2, h4, h1