## Slide 1: Power Plant Technology Combined Cycle and Renewable Energy Power Systems (Lecture 2)
by
Mohamad Firdaus Basrawi, Dr. (Eng) Mechanical Engineering Faculty mfirdausb@ump.edu.my

## Slide 2
Biogas-fuelled Cogeneration System in
Sewage Treatment Plants
Why Biogas?
Advantage:
Biomass is abundant
Renewable
Carbon zero
Disadvantage:
Low energy density (scattered in a wide range)
food supply problem
Waste type of biomass has high potential

## Slide 3
Annual production rate of waste type biomass in Japan
Sludge is already collected in a central plant. There are many STPs that can produce biogas and the number is increasing
Anaerobic digestion that can produce biogas is a common practice in middle- and large-scale plant, and small-scale plant also in the future
Why Sewage Treatment Plant

## Slide 4
出典)国土交通省，下水道，2006
Small- and middle scale：8plants
Large scale：23plants
Only 30plants generate power
There are about1900 sewage treatment plant
Power generation in Small- and middle-scale plant is not widespread
Even large-scale plants do not efficiently use waste heat
Current status of biogas utilization for power generation

## Slide 5
Anaerobic Digestion
Sludge
Biogas
Boiler
Heat
Incineration
Sewage Treatment Plant
Current status in Small- and middle-scale plants
Why small- and middle-scale plants do not generate power?
Cost time and money needed to purify biogas due to impurities in biogas
Lack of power generator that has capacity lower than a few hundred kWs
  Biogas production amount is small．
  Biogas heating value is low．
Power generator that has capacity less than a few hundred kWs are needed
Sewage water
Clean water

## Slide 6
Capacity lower than300kW
Low maintenance cost
Low emissions (NOx)
High efficiency (recuperator)
High power density
Micro Gas Turbine (MGT)

## Slide 7
Anaerobic Digestion
Sludge
Biogas
Boiler
Heat
Inceneration
Sewage Treatment Plant
Current status of power generation in sewage treatment plants
Electricity
Even large-scale plants do not efficiently use waste heat

## Slide 8
Biogas production and heat demand varies depend on the season.
Biogas
Electricity
Heat
CGS
Cover all heat demand (replace boiler)
Cover some portion of power demand
CGS
Anaerobic Digestion
Sludge
Biogas
Sewage Treatment Plant
Better utilization of biogas in sewage treatment plants

## Slide 9
Biogas production and heat demand varies depend on the season.
Biogas
Electricity
Heat
CGS
CGS: MGTs has its characteristics (performance at partial load, scale, etc)
STP: STPs has its own characteristics, heat demand, biogas production, scale, etc.)
Efficient combination method and its performance is not well clarified
Problems Statement
Anaerobic Digestion
Sludge
Biogas
Sewage Treatment Plant

## Slide 10
Biogas production and heat demand varies depend on the season.
Biogas
Electricity
Heat
CGS
CGS: MGTs has its characteristics (performance at partial load, scale, etc)
STP: STPs has its own characteristics, heat demand, biogas production, scale, etc.)
Efficient combination method and its performance is not well clarified
Problems Statement
Anaerobic Digestion
Sludge
Biogas
Sewage Treatment Plant
Clarifies performance of MGT-CGSs
Objectives
Clarifies efficient utilization of biogas-fuelled CGS

## Slide 11
-
20
-
10
0
10
20
30
40
Ambient Temperature[℃]
East Hokkaido
Okinawa
Tokyo
2004/01
Times [year/month]
2005/01
2006/01
2007/01
2008/01
Winter (6Months):
-25 ~5℃
Ambient temperature in 2004-2008
Research location
http://0429.jp/archives/2007/12/00131.php

## Slide 12
Research location
http://www.geocities.jp/ucyama76/photo04ooyuki.htm

## Slide 13
Research location
http://www.geocities.jp/ucyama76/photo04ooyuki.htm
http://ameblo.jp/e-start21/archive2-200901.html
http://blog.livedoor.jp/shimagare/archives/51000546.html

## Slide 14
http://higasikoshi.blog.so-net.ne.jp/2012-07-04
http://schatzkiste.blog18.fc2.com/blog-entry-121.html
http://blog-tourismmalaysia.jp/archives/51836814.html
Research location

## Slide 15
Overall energy system in the middle-scale sewage treatment plant
Recovered
heat
Electrical power grid
Boiler
Biogas for CGS
power
server
Electrical power from CGS
Biogas for boiler
Admin.
Building
EHE
Exhaust
heat
MGT
CGS
Electricity and heat demand
Gas
tank
Digester
Tank
EHE :Exhaust heat exchanger
Gas pre-
treatment

## Slide 16
Recovered
heat
Electrical power grid
Boiler
Biogas for CGS
power
server
Electrical power from CGS
Biogas for boiler
Admin.
Building
EHE
Exhaust
heat
MGT
CGS
Electricity and heat demand
Gas
tank
Digester
Tank
EHE :Exhaust heat exchanger
Gas pre-
treatment

## Slide 17
50
55
60
65
70
75
80
85
Conv.
A1
A2.a
A2.b
A3.a
A3.b
A4
Electricity
Heat
Biogas energy recovery
efficiency, ηb.e.r, heat [%]
73.8%
73.7%
74.4%
76.8%
77.9%
78.2%
59.8%
4000
5000
6000
7000
8000
HP
MH
Deficiency of Electrical Power
Conv.
A1
A2.a
A2.b
A3.a
A3.b
A4
Electrical Demand [kW/year]
28.3%
30.0%
30.6%
0%
23.2%
23.1%
24.2%
Some of the results
-Biogas can be a usefull source of energy to generate electricity.
-But, electricity used can only cover a part of power demand in the facility.
-The facility has various equipment (compressor, pump, lighting, etc) and has high power demand.
-The scenario is basically same for any facility (solid municipal waste facility, etc).

## Slide 22
CL4
IPP proposed a CCGT with parameters shown below:
Capacity: 300MW
Gas Turbine pressure ratio: 10
Inlet air temperature: 30oC
Max gas temperature: 1000oC
HRSG outlet temperature (Gas side): 110oC
Condition of Steam Turbine Inlet: 80 Bar, 500oC
Condenser pressure: 0.1 Bar
cp,air: 1.005 kJ/kgK
cp,gas: 1.15 kJ/kgK
kair: 1.4
kgas: 1.33
Fuel heating value: 43.2 MJ/kg
Claimed CCGT performance are as shown below. Verify its performance using parameters above;
Wnet, GC: 210MW
Wnet, SC: 90MW
Overall efficiency: 64%
Air-fuel ratio: 55