## Contoh 1
FAKULTI KEJURUTERAAN ELEKTRIK & ELEKTRONIK
UNIVERSITI MALAYSIA PAHANG (UMP)
26600 PEKAN, PAHANG, MALAYSIA
LOW VOLTAGE ELECTRICAL INSTALLATION
Question:
One unit small factory need a new installation of industrial wiring with three phase supply 415V/50hz.
The owner has a plan to install the following loads :
25 ´ 36 Watt Pendaflour lamp
3 ´ 18 Watt pendaflour lamp
2 ´ 60 Watt Filemen lamp
12 ´ 13A Socket outlet - Radial circuit
1 ´ 3.3 kW Water heater
1 ´ 1.8 kW Water heater
1 ´ 2.2 kW Water heater
1 ´ 2 kW Electric cooker
1 ´ 1.5 hp single phase Air-cond
1 ´ 2.5 hp three phaseAir-cond
1 ´ 4 hp three phase Air-cond
2 ´ 5 pin isolator
1 ´ 12 V Electric door bell
1 ) | Calculate the Full Load Current and Estimation Current for all load by reffering the table 4B
2 ) | Draw the schematic single line diagram for the installation including the right size cable
and the current rating for all the protection equipment
Answer :
LOAD |  |  | FULL LOAD CURRENT |  | ESTIMATION CURRENT
1) Lighting |  |  |  | For all pendaflour lamp are using choke | Refer table 4B : No.1
a ) Pendaflour lamp |  |  | I = P |  | 90% from current demand
25 ´ 36 W |  | = 900 W | V
3 ´ 18 W |  | = 54 W | I = 954 | ´ 1.8 = 7.15 A | * Total lighting current = 7.65 A
|  | 954 W | 240 |  | * 90% ´ 7.65 A = 6.89 A
b ) Filemen lamp
2 ´ 60 W |  | = 120 W | I = 120 = 0.5 A
240
|  |  | Total = 7.65 A |  | Total = 6.89 Amp
2 ) Socket outlet 13 Amp. |  |  |  |  | Refer table 4B : No.9
12 ´ 13 A - radial circuit |  |  | 3 radial circuit |  | 100% bigger = 32 A
|  |  | = 3 ´ 32A ( MCB ) |  | 50% the rest of usage
|  |  | = 96 A |  | * 2 x 50 ´ 32A = 32 A
100
|  |  | Total = 96 A |  | * Total = 64 A
3) 5 Pin Isolator |  |  |  |  | Refer table 4B : No.10
2 x 5 pin isolator |  |  | 2 x 32A (MCB) |  | 100% bigger = 32 A
|  |  | = 64 A |  | 75% the rest of usage
* 75 ´ 32A = 24 A
100
|  |  | Total = 64 A |  | * Total = 56 A
Refer table 4B : No.5
4 ) Water heater |  |  | I = 3.3kW = 13.75 A
1 ´ 3.3 kW |  |  | 240 V |  | 100% bigger = 13.75 A
1 ´ 1.8 kW |  |  | I = 1.8kW = 7.5 A |  | 100% 2nd bigger = 9.17 A
1 ´ 2.2 kW |  |  | 240 V |  | 25% the rest of usage
|  |  | I = 2.2kW = 9.17 A |  | * 25 ´ 7.5 = 1.87 A
|  |  | 240 V |  | 100
|  |  | Total = 30.42 A |  | Total = 25.54 Amp
3 ) Electric Cooker |  |  | I = 2kW |  | Refer table 4B : No.3
2 kW |  |  | 240 V |  | 100% bigger = 8.33 A
= 8.33 A
|  |  | Total = 8.33 A |  | Total = 8.33 A
4 ) Air-cond |  |  | 1.5 hp |  | Refer table 4B : No.4
1 ´ 1.5 hp 1-Ø A/C |  |  | I = 1119 W = 4.66 A |  | 100% bigger = 7.19 A
1 ´ 2.5 hp 3-Ø A/C |  |  | 240 V |  | 80% 2nd bigger
1 ´ 4 hp 3-Ø A/C |  |  | 2.5 hp |  | * 80 ´ 4.49 = 3.59 A
|  |  | I = 1865 W = 4.49 A |  | 100
* 1 hp = 746 W |  |  | 415 V |  | 60% the rest of usage
| 1.5 hp = 1119 W |  | 4 hp |  | * 60 ´ 4.66 = 2.8 A
| 2.5 hp = 1865 W |  | I = 2984 W = 7.19 A |  | 100
| 4 hp = 2984 W |  | 415 V
|  |  | Total = 16.34 A |  | Total = 13.58 A
Electric door bell
Neglectable |  |  |  | Neglectable
TOTAL |  |  | 222.74 A |  | 174.34 A
|  |  | 3 Phase |  | 3 Phase
|  |  | 74.25 A |  | 58.11 A

## Skematik Contoh 1
GAMBARAJAH LITAR SKEMATIK |  |  | BUS BAR
6A
10 x 36W Pendaflor lamp
6A
10 x 36W Pendaflor lamp
|  |  | 6A |  | 5 x 36W Pendaflor lamp
3 x 18W Pendaflor lamp
2 x 60W Filemen lamp
32A
4 x 13A Socket outlet - Radial Circuit
3 x 63 Cut-Out
| Fuse |  | 32A
VOLTAGE |  |  |  |  | 4 x 13A Socket outlet - Radial Circuit
SOURCE
3 Phase 415 V/50Hz |  |  | 32A
| Neutral |  |  |  | 4 x 13A Socket outlet - Radial Circuit
Link
32A
|  | 4 x 16mm2 |  |  | 1 x 2 kW Electric Cooker
|  |  | 20A | 10mA
1 x 3.3 kW Water heater
|  |  | 20A | 10mA
25 ´ 36 Watt Pendaflor lamp |  |  |  |  | 1 x 1.8kW Water heater
3 ´ 18 Watt Pendaflor lamp
2 ´ 60 Watt Filemen lamp |  |  | 20A | 10mA
12 ´ 13A Socket outlet - Radial Circuit |  |  |  |  | 1 x 2.2kW Water heater
1 ´ 3.3 kW Water heater
1 ´ 1.8 kW Water heater |  |  | 20A
1 ´ 2.2 kW Water heater |  |  |  |  | 1 x 1.5 hp Air-cond
1 ´ 2 kW Electric Cooker |  |  | 20A
2 ´ 5 pin isolator |  |  |  |  | 1 x 2.5 hp Air-cond
1 ´ 1.5 hP 1-Ø Air-cond |  |  | 20A
1 ´ 2.5 hP 3-Ø Air-cond |  |  |  |  | 1 x 4 hp Air-cond
1 ´ 4 hP 3-Ø Air-cond
1 ´ 12 V Electric door bell |  |  | 2A
1 x 12 V Electric door bell
32A
1 x 5 pin isolator
32A
1 x 5 pin isolator
2 x 1.5mm2
2 x 4mm2
4 x 4mm2
kWh
KiloWatt Meter
Main Switch
40A / 60A
TPN 63A ELCB 100mA

## Table 4B English
Schedule Provisions for Diversity
Table 4B
The purpose of the final circuit is connected from the conductor or the switch gear which applies diversity | Types of premise
| Installation of individual homes, including a row of individual housing | Small shops, offices and commercial buildings | Small hotels, guesthouses etc.
1 ) Exposure/Lighting | 66 % of total of current | 90 % of total of current | 75 % of total of current
| demand | demand | demand
| 100% of the total extent of 10 Amp current demand. + 50% of any current demand exceeds 10 Amp. | 100% of the excess factor of the largest equipment + 75% of the remaining factors of surplus equipment. | 100% of the excess factor of the largest equipment + 80% surplus factor for the second-largest equipment + 60% surplus factor for the remaining equipment.
2 ) Heating and power
usage. Refer to item #3
to #8 (below).
| 10 Amp. + 30% surplus factor for the cooking appliance is connected to more than 10 Amp. + 5 Amp. If the socket outlets are jointed in the unit. | 100% of the excess factor of the largest equipment + 80% surplus factor for the second-largest equipment + 60% surplus factor for the remaining equipment.
3 ) Cooking equipments
|  | 100% of the surplus factor | 100% of the surplus factor
4 ) Motors other than |  | for the largest motor + | for the largest motor +
the elevator motors | No diversity | 80% for the second | 50% surplus factor for the
that are subject to |  | largest motor + 60% | remaining motors.
special consideration. |  | of the remaining motors.
100% of the largest appliance + 100% surplus factor for the second-largest equipment + 25% surplus factor for the remaining equipment.
5 ) Water heater
( immediately type )
6 ) Water heater (controlled | No provision of diversity
by a thermostat )
7 ) Installation of floor | No provision of diversity
heater
8 ) Channels installation of | No provision of diversity
thermal heating space
9 ) The composition of | 100 % for required current | 100 % for required current of the biggest circuit + 50%
the final circuit using | of the bigest circuit + | of required current for others circuit.
a standard socket outlet. | 40 % of required
current for others circuit.
10 ) Outlet sockets | 100% of current demand | 100% of current demand | 100% of current demand
other than that found | point of largest | point of largest consump- | point of largest consumption
in 9 above and fixed | consumption + 40% of | tion + 75% of current | + 75% of current demand
equipment other than | current demand for each | demand for each others | for each of the main rooms
those mentioned above. | others point of | point of consumption. | (dining room, etc..) + 40%
| consumption. |  | of current demand for each
use of the other points.
* For the purposes of this Schedule, the water heater instant water heater is deemed to be such a burden only
when the pipe heats the water in the open and thus the intermittent electricity.
* It is important to ensure that the proportional distribution board is sufficient to take the total load connected
to it without the use of any variety.