## Slide 1: BSB3503 - Biomanufacturing CHAPTER 10 GMP – Laboratory & Production Area (HVAC)
Author: Nurul Azyyati Sabri
Co-Author / Editor: Rama Yusvana Faculty Industrial Sciences & Technology yusvana@ump.edu.my

## Slide 2: HVAC system for clean room (Design and Practice)
HVAC system and ISO classes for clean room
Characterization of HVAC system
Air Filtration and Distribution
2

## Slide 3
211.46 “Ventilation, air filtration, air heating and cooling”
“Adequate ventilation should be provided”.
“Equipment for adequate control over air pressure, micro-organisms, dust, humidity, and temperature shall be provided when appropriate for the manufacture, processing, packing, or holding of a drug product”
Notes: FDA's latest, Non-Penicillin Beta-Lactam Drugs: A CGMP Framework for Preventing Cross-Contamination, is aimed at non-penicillin drugs characterized by a beta-lactam ring, a chemical structure common to many types of antibiotics including caphalosporins, monobactams, penems, carbapenems and penicillin. - See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
ne of the main problems associated with the manufacture of these drugs is their propensity to cross-contaminate one another if not properly separated. While problematic for its own sake, the contamination can create additional problems as well at the user level if not properly controlled, FDA explained. That's because some people are hypersensitive to penicillin and can have an "exaggerated allergic immune response" if exposed to the drug, potentially resulting in death.
As a result, manufacturers need to take extreme care to make sure that the manufacture of penicillin takes place in entirely separate facilities, FDA recommended.
- See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
3

## Slide 4
211.46 Ventilation, air filtration, air heating and cooling
“Air filtration system, including pre-filters and particulate matter air filters, shall be used when appropriate on air supplies to production areas, measures shall be taken to control recirculation of dust from production. In areas where air contamination occurs during production, there shall be adequate exhaust systems adequate to control contaminants”.
Notes: FDA's latest, Non-Penicillin Beta-Lactam Drugs: A CGMP Framework for Preventing Cross-Contamination, is aimed at non-penicillin drugs characterized by a beta-lactam ring, a chemical structure common to many types of antibiotics including caphalosporins, monobactams, penems, carbapenems and penicillin. - See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
ne of the main problems associated with the manufacture of these drugs is their propensity to cross-contaminate one another if not properly separated. While problematic for its own sake, the contamination can create additional problems as well at the user level if not properly controlled, FDA explained. That's because some people are hypersensitive to penicillin and can have an "exaggerated allergic immune response" if exposed to the drug, potentially resulting in death.
As a result, manufacturers need to take extreme care to make sure that the manufacture of penicillin takes place in entirely separate facilities, FDA recommended.
- See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
4

## Slide 5
211.46 “Ventilation, air filtration, air heating and cooling”
“Air-handling systems for the manufacture, processing and packing of PENICILIN shall be completely separate from those for other drug, products for human use”.
Notes: FDA's latest, Non-Penicillin Beta-Lactam Drugs: A CGMP Framework for Preventing Cross-Contamination, is aimed at non-penicillin drugs characterized by a beta-lactam ring, a chemical structure common to many types of antibiotics including caphalosporins, monobactams, penems, carbapenems and penicillin. - See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
ne of the main problems associated with the manufacture of these drugs is their propensity to cross-contaminate one another if not properly separated. While problematic for its own sake, the contamination can create additional problems as well at the user level if not properly controlled, FDA explained. That's because some people are hypersensitive to penicillin and can have an "exaggerated allergic immune response" if exposed to the drug, potentially resulting in death.
As a result, manufacturers need to take extreme care to make sure that the manufacture of penicillin takes place in entirely separate facilities, FDA recommended.
- See more at: http://www.raps.org/focus-online/news/news-article-view/article/3201/#sthash.2V10N42U.dpuf
5

## Slide 6
Ǿ 211.42 “Design and Construction features” Part (c) cont
Aseptic processing, which include as appropriate:
  Floors, walls, and ceilings
  Temperature and humidity controls
  An air supply filtered through high-efficiency particular air filters
Notes: 6

## Slide 7
Ǿ 211.42 “Design and Construction features” Part (c) cont
Aseptic processing, which include as appropriate:
  A system for monitoring environmental conditions
  A system for cleaning and disinfecting the room
  A system for maintaining any equipment.
Notes: 7

## Slide 8: ISO Classification of Clean Room
ISO | FED STD 209 | 0.1 μm | 0.2 μm | 0.3μm | 0.5 μm | 5.0 μm
Class 3 | 1 | 1000/35 |  |  | 35/1 | 0
Class 4 | 10 | 10, 000/345 | 75 | 30 | 352/10 | 0
Class 5 | 100 | 100, 000/3450 | 750 | 300 | 3520/100 | 0
Class 6 | 1,000 | 1, 000, 000/34,500 | N/A | N/A | 35,200/1000 | 7
Class 7 | 10, 000 | 345,000 | N/A | N/A | 352,000/10,000 | 70
Class 8 | 100,000 | 3,450,000 | N/A | N/A | 3,520,000/100,000 | 700
ISO 14644-1 (Per cubic meter)
Fed Std. 209 E. USA (per cubic feet)
ISO standard requires results to be shown in cubic meters (1 cubic meter=35.314 cubic feet)
8

## Slide 9: Factors Determining the Operation Parameters of Cleanrooms
Air Flow
Heating and Cooling Capacities
Room Internal Design
Differential Pressure and Air Lock
9

## Slide 10: 1. “Air Flow”
20 to 40 m3 air changes per hour for Class 10,000 or 100,000 requirements
To achieve Class 100 requirements carried out only by using vertical undirectional flow
10

## Slide 11: 1. “Air Flow”
“Class 100 requires 20 times more airflow than a class 10,000 clean room”
Energy costs
11

## Slide 12: 2. Heating and Cooling Capacities
Temperature Range: 18 to 220C and 30 to 50% Relative Humidity for class 100 and 10000
Satisfactory for controlling microbial growth and resonable worker comfort
12

## Slide 13: 2. Heating and Cooling Capacities
Low temp (20C to 80C) to meet some requirements.
Must also consider other factors or variations.
13

## Slide 14: 3. Room Internal design
“Adequate positioning of the air delivery inlets and outlets”
14

## Slide 15: 3. Room Internal design
Affect the “time required to recover the room classification after contamination with a chemical aerosol”
Can use of “nonviable particle counting devices”.
15

## Slide 16: 4. Differential Pressure and Air Lock
Maintaining the cleanliness of the room
The design should be of sufficient flow velocity
16

## Slide 17: 4. Differential Pressure and Air Lock
Interlocking system
Air Shower System, location and design
Differential Pressure between adjacent manufacturing areas
17

## Slide 18: “Recommended Criteria for Biosafety Levels 2 and 3”
Biosafety Level | Agents | Practice | Safety Requirements (Primary Barriers) | Facilities (Secondary Barriers)
2 | “Associated with human disease. Hazards comes from autoinoculation, ingestion mucous membrane exposure” | “Standard Microbiological Practice plus: -Biohazards sign Sharps precautions Biosafety manual defining any needed waste decontaminating or medical surveillance policies” | “Primary barriers involving Class 1 physical containment devices used for all manipulations of agents cause by splashes or aerosols of infectious materials; personnel protection equipment involving protective lab, clothing , gloves, respiratory protection when required” | “Open bench top sink required plus autoclave available”
3 | “Indigenous or exotic agents with potential for aerosol transmission; disease may have serious or lethal consequences” | Similar to “BL-2” | Similar to “BL-2” | “BL-2” plus “Physical separation from access corridor, Self-closing double door access, Exhaust air not recirculated, Negative airflow into laboratory”
18

## Slide 19: Differential Pressure
Pressure differential is a key ingredient in cleanrooms and clean zones.
Control airborne contaminants.
Negative Pressure is achieved when air is evacuated to an area, room or hood.

## Slide 20
Laminar flow hoods often use negative pressure.
Evacuated air is either exhausted or run through a series of filters and returned to the chamber / room.
Differential Pressure

## Slide 21
Very important to have filtered air returning to the area.
Ensures a clean work area.
Differential Pressure

## Slide 22
Positive pressure areas are generally used in cleanrooms.
To supply an area with enough clean, filtered air to keep contaminants from entering the room or area.
Reducing cross-contamination.
Differential Pressure

## Slide 23: 1- “Class A and B (Kept at positive air pressure)”
Room Function
“Filtration of inactivated product, filling, formulation, sterile storage and nonpathogenic virus replication if aseptic processing, purification, if required by the process, aseptic media preparation. This room is equipped with a class 100 (Class A) laminar airflow hood”.
23

## Slide 24: 1- “Class A and B (Kept at positive air pressure)”
Room Access:
- “Materials Air Lock IN”
- “Materials Air Lock OUT with fumigation for live organism handling area”
24

## Slide 25: 2- “Class B (Kept at negative air Pressure)”
Room Function:
“Culture of pathogenic virus and inactivation of pathogenic virus if aseptic Operations, purification if requested by the process. Room is equipped with class A laminar airflow cabinet”
25

## Slide 26: 2- “Class B (Kept at negative air Pressure)”
Room Access:
- “Materials Air Lock IN”
- “Materials Air Lock OUT (with fumigation)”
26

## Slide 27: 3- “Class C (Kept at positive air pressure)”
Room Function:
Bioreactor culture
Purification of non-pathogenic products,
Clean material
Storage
Media preparation
27

## Slide 28: 3- “Class C (Kept at positive air pressure)”
Room Access:
Personnel Air Lock two doors
“The access to media preparation production rooms proceeds via an Air lock if the facility is designed for cell culture and viral replication”
28

## Slide 29: 4- “Class C (Kept at negative air pressure)”
Room Function:
Bioreactor culture
Purification of pathogenic products
(production room classified as “BL3”)
29

## Slide 30: 4- “Class C (Kept at negative air pressure)”
Room Access:
- “Materials Air Lock IN”
- “Materials Air Lock OUT (with fumigation)”
30

## Slide 31: What is Pressure Cascade?
“A process whereby air flows from the cleanest area, which is maintained at the highest pressure to a less clean area at lower pressure”.
31

## Slide 32: Pressure Cascade
Dirty Environment
(Ambient Pressure)
15 Pa pressure Difference
More Clean Environment
(Higher Pressure)
15 Pa pressure Difference
Cleanest Environment
(Higher Room Pressure)
32

## Slide 33: Operating parameters for Class B kept at positive air pressure
Parameters | Area |  |  |  | 
 | Production room | Material AL IN | Material AL OUT | Personnel AL 1 | Personnel AL 2
Pressure (Pa) | +45 | (a) | (b) | +30 | (e)
Min Change (AC/h) | 40 | 200 | 200 | 20 | 600
“Decontamination time (min)” | 15 | 3 | 3 | 12 | 1
“Partial Air Recycling” | Yes | 100% | (c) | YES | 100%
“Temperature (oC)” | 18-22 | NA | (d) | 18-22 | 18-22
RH (%) | 30-50 | NA | (d) | 40-60 | 40-60
“Air Delivery Filter (% DoP Retention)” | 99, 950 | 99, 995 | 99, 995 | 99, 995 | 99, 995
“Air Exhaust Filter” | 99, 995 | G 85 | G 85 | G 85 | G 85
“Location of Delivery Inlet” | Ceiling | Ceiling | Ceiling | Ceiling | Ceiling
“Location of Exhaust Outlet” | Bottom of Wall | Bottom of Wall | Bottom of Wall | Ceiling | Bottom of Wall
“Fumigation” | YES | YES | YES | NO | YES
33

## Slide 34
Operating Parameters for Class B kept at negative air pressure
Parameters | Area |  |  |  |  | 
 | Production room | Material AL IN | Material AL OUT | Personnel AL 1 | Personnel AL 2 | Personnel AL 3
Pressure (Pa) | -30 | (a) | (b) | +30 | -30 | -15
Min Change (AC/h) | 40 | 200 | 200 | 20 | 20 | 600
“Decontamination time (min)” | 15 | 3 | 3 | 12 | 12 | 1
“Partial Air Recycling” | Yes | 100% | (c) | YES | NO | NO
“Temperature (oC)” | 18-22 | NA | (d) | 18-22 | 18-22 | 18-22
“RH (%)” | 30-50 | NA | (d) | 40-60 | 40-60 | 40-60
“Air Delivery Filter (% DoP Retention)” | 99, 950 | 99, 995 | 99, 995 | 99, 995 | 99, 995 | 99, 995
“Air Exhaust Filter” | 99, 995 | G 85 | G 85 | G 85 | G 85 | 99, 995
“Location of Delivery Inlet” | Ceiling | Ceiling | Ceiling | Ceiling | Ceiling | Ceiling
“Location of Exhaust Outlet” | Bottom of Wall | Bottom of Wall | Bottom of Wall | Ceiling | Bottom of Wall | Bottom of Wall
“Fumigation” | YES | YES | YES | NO | YES | YES
34

## Slide 35
Operating parameters for Class C kept at positive air pressure
Parameters | Production Room | Air lock (a)
Pressure (Pa) | +30 | (b)
Min Change (AC/h) | 20 | 20
“Decontamination time (min)” | 12 | 3
“Partial Air Recycling” | YES | YES
“Temperature (oC)” | 18-22 | 18-22
“RH (%)” | 40-60 | NA
“Air Delivery Filter (% DoP Retention)” | 99, 995 | 95
“Air Exhaust Filter” | G 85 | G 85
“Location of Delivery Inlet” | Ceiling | Ceiling
“Location of Exhaust Outlet” | Bottom of wall | Bottom of Wall
“Fumigation” | Occasional | Occasional
35

## Slide 36
Operating Parameters for Class C kept at negative air pressure
Parameters | Production Room | Air lock (a)
Pressure (Pa) | -15 | -30
Min Change (AC/h) | 20 | 20
“Decontamination time (min)” | 12 | 3
“Partial Air Recycling” | NO | NO
“Temperature (oC)” | 18-22 | 18-22
“RH (%)” | 40-60 | NA
“Air Delivery Filter (% DOP Retention)” | 99, 995 | 95
“Air Exhaust Filter” | 99, 995 | G 85
“Location of Delivery Inlet” | Ceiling | Ceiling
“Location of Exhaust Outlet” | Bottom of wall | Ceiling
“Fumigation’ | YES | YES
36

## Slide 37
Operating Parameters for Class D
Parameters | Production Room
Pressure (Pa) | Steps of 15 pa
Min Change (AC/h) | 20
“Decontamination time (min)” | 3
“Partial Air Recycling” | YES
“Temperature (oC)” | 18-22
“RH (%)” | 40-60
“Air Delivery Filter (% DOP Retention)” | 95
“Air Exhaust Filter” | G 85
“Location of Delivery Inlet” | Ceiling
“Location of Exhaust Outlet” | Bottom of wall
“Fumigation” | Occasional
37